## Benchmark
Provided for Reference Only
| UC Benchmark Site Energy (kBtu/yr/GSF) | Annual Electricity1 | Annual Thermal4 | Max. Power2 | Max. Chilled Water3 | Max. Thermal4
|  | kWh/yr/GSF | therms/yr/GSF | W/GSF | tons/kGSF | therms/hr/GSF
|  | Including Prorated Part of Plant Use and Site Lighting | Including Prorated Part of Plant Use | Includes Prorated Part of Small Peak (Pumping) Load at Plant | Load on Plant | Including Prorated Part of Plant Use
Academic/Administrative Non-complex Space
UC Berkeley | 59.0834 | 11.2121 | 0.20828 | 2.144 | 1.5314 | 0.12401
UC Davis | 65.8952 | 13.3125 | 0.20473 | 3.3272 | 2.5017 | 0.12401
UC Irvine | 60.543 | 12.9797 | 0.16256 | 2.5616 | 1.926 | 0.12401
UCLA | 59.1238 | 12.3333 | 0.17043 | 2.2832 | 1.7167 | 0.12401
UC Merced | 68.5814 | 14.3489 | 0.19623 | 3.4665 | 2.6064 | 0.12401
UC Riverside | 65.2921 | 13.8762 | 0.17946 | 3.3272 | 2.5017 | 0.12401
UC San Diego | 57.7253 | 12.2294 | 0.15999 | 2.2136 | 1.6644 | 0.12401
UCSF - Parnassus | 59.1786 | 11.1124 | 0.21263 | 2.0048 | 1.5074 | 0.12401
UCSF - Mission Bay | 60.2633 | 11.4304 | 0.21263 | 2.144 | 1.5314 | 0.12401
UC Santa Barbara | 58.4885 | 11.4918 | 0.19278 | 2.2136 | 1.6644 | 0.12401
UC Santa Cruz | 60.4927 | 11.1082 | 0.22591 | 2.2136 | 1.5812 | 0.12401
Housing Non-complex Space
UC Berkeley | 56.5329 | 7.8484 | 0.29754 | 1.5008 | 1.072 | 0.17716
UC Davis | 61.0427 | 9.3187 | 0.29247 | 2.3291 | 1.7512 | 0.17716
UC Irvine | 54.224 | 9.0858 | 0.23223 | 1.7931 | 1.3482 | 0.17716
UCLA | 53.8036 | 8.6333 | 0.24347 | 1.5983 | 1.2017 | 0.17716
UC Merced | 62.3037 | 10.0442 | 0.28033 | 2.4265 | 1.8244 | 0.17716
UC Riverside | 58.7796 | 9.7134 | 0.25638 | 2.3291 | 1.7512 | 0.17716
UC San Diego | 52.0639 | 8.5606 | 0.22855 | 1.5495 | 1.1651 | 0.17716
UCSF - Parnassus | 56.9165 | 7.7787 | 0.30376 | 1.4034 | 1.0552 | 0.17716
UCSF - Mission Bay | 57.6758 | 8.0013 | 0.30376 | 1.5008 | 1.072 | 0.17716
UC Santa Barbara | 54.9876 | 8.0443 | 0.2754 | 1.5495 | 1.1651 | 0.17716
UC Santa Cruz | 58.8044 | 7.7757 | 0.32274 | 1.5495 | 1.1068 | 0.17716
Lab/Complex Space5
UC Berkeley | 306.2419 | 36.0378 | 1.8328 | 5.2852 | 3.7752 | 0.42809
UC Davis | 311.8138 | 37.7951 | 1.8286 | 6.2752 | 4.7182 | 0.42809
UC Irvine | 305.8239 | 37.5167 | 1.7782 | 5.6346 | 4.2366 | 0.42809
UCLA | 304.9186 | 36.9758 | 1.7876 | 5.4017 | 4.0614 | 0.42809
UC Merced | 313.7565 | 38.6622 | 1.8184 | 6.3917 | 4.8058 | 0.42809
UC Riverside | 310.4032 | 38.2668 | 1.7984 | 6.2752 | 4.7182 | 0.42809
UC San Diego | 303.3741 | 36.8889 | 1.7751 | 5.3435 | 4.0177 | 0.42809
UCSF - Parnassus | 306.4775 | 35.9544 | 1.838 | 5.1688 | 3.8863 | 0.42809
UCSF - Mission Bay | 307.3851 | 36.2204 | 1.838 | 5.2852 | 3.7752 | 0.42809
UC Santa Barbara | 305.1886 | 36.2719 | 1.8143 | 5.3435 | 4.0177 | 0.42809
UC Santa Cruz | 308.0534 | 35.9509 | 1.8539 | 5.3435 | 3.8168 | 0.42809
100% Lab Space6
UC Berkeley | 553.4004 | 60.8635 | 3.4573 | 8.4265 | 6.0189 | 0.73217
UC Davis | 557.7325 | 62.2777 | 3.4524 | 9.2231 | 6.9347 | 0.73217
UC Irvine | 551.1048 | 62.0537 | 3.3938 | 8.7076 | 6.5471 | 0.73217
UCLA | 550.7133 | 61.6184 | 3.4047 | 8.5202 | 6.4062 | 0.73217
UC Merced | 558.9316 | 62.9756 | 3.4406 | 9.3169 | 7.0052 | 0.73217
UC Riverside | 555.5144 | 62.6573 | 3.4173 | 9.2231 | 6.9347 | 0.73217
UC San Diego | 549.0228 | 61.5485 | 3.3902 | 8.4733 | 6.3709 | 0.73217
UCSF - Parnassus | 553.7765 | 60.7964 | 3.4634 | 8.3327 | 6.2652 | 0.73217
UCSF - Mission Bay | 554.5069 | 61.0105 | 3.4634 | 8.4265 | 6.0189 | 0.73217
UC Santa Barbara | 551.8887 | 61.0519 | 3.4358 | 8.4733 | 6.3709 | 0.73217
UC Santa Cruz | 555.6142 | 60.7936 | 3.4819 | 8.4733 | 6.0524 | 0.73217
Building-Specific Adjustments
1 These values may be slightly lower than previously published values (i.e. for UC Merced) because they reflect load on the building meter instead of at the campus meter. To reflect load on campus meter, increase value by 1.05 (to account for distribution and transformation losses).
2 These values may be slightly lower than previously published values (i.e. for UC Merced) because they reflect load on the building meter instead of at the campus meter. To reflect load on campus meter, increase value by 1.05 (to account for distribution and transformation losses). For campuses with district chilled water, if a specific building has a chiller instead, increase value by (1/0.7).
3 In the case where a chiller is in the building, add the maximum chilled water value to the maximum power value by multiplying the chilled water value times 0.6 kW/ton.
4 These benchmarks are directly applicable to buildings with boilers in the building or connected to (low-loss) district hot water systems (non-steam). These benchmarks can be applicable to building design for buildings connected to district steam systems with the understanding that additional losses characteristic of steam systems will impact actual building energy performance during operations. For example, 50% extra use from trap/exchanger losses within the building plus 50% extra use from trap/leakage losses in distribution systems has been commonly observed.
5 Benchmark values shown are valid for complex space consisting of 50% lab use and 50% academic / administrative use. For additional information on calculating EUI for different levels of complex space see "100% Lab Space" values.
6 The 100% Lab Space benchmark values are provided for use in creating a custom benchmark and target when a building project contains significantly more or less lab space than the 50% lab use and 50% academic/administrative use outlined in the Lab/Complex Space section.

## 2015-16
Provided for Reference Only
| 2015-16 Compliance Target - 65% of Benchmark Site Energy (kBtu/yr/GSF) | Annual Electricity1 | Annual Thermal4 | Max. Power2 | Max. Chilled Water3 | Max. Thermal4
|  | kWh/yr/GSF | therms/yr/GSF | W/GSF | tons/kGSF | therms/hr/GSF
|  | Including Prorated Part of Plant Use and Site Lighting | Including Prorated Part of Plant Use | Includes Prorated Part of Small Peak (Pumping) Load at Plant | Load on Plant | Including Prorated Part of Plant Use
Academic/Administrative Non-complex Space
UC Berkeley | 38.4042 | 7.2878 | 0.13538 | 1.3936 | 0.99544 | 0.099209
UC Davis | 42.8319 | 8.6531 | 0.13307 | 2.1627 | 1.6261 | 0.099209
UC Irvine | 39.353 | 8.4368 | 0.10567 | 1.6651 | 1.2519 | 0.099209
UCLA | 38.4305 | 8.0166 | 0.11078 | 1.4841 | 1.1159 | 0.099209
UC Merced | 44.5779 | 9.3268 | 0.12755 | 2.2532 | 1.6941 | 0.099209
UC Riverside | 42.4398 | 9.0195 | 0.11665 | 2.1627 | 1.6261 | 0.099209
UC San Diego | 37.5215 | 7.9491 | 0.10399 | 1.4389 | 1.0818 | 0.099209
UCSF - Parnassus | 38.4661 | 7.2231 | 0.13821 | 1.3031 | 0.9798 | 0.099209
UCSF - Mission Bay | 39.1711 | 7.4297 | 0.13821 | 1.3936 | 0.99544 | 0.099209
UC Santa Barbara | 38.0175 | 7.4697 | 0.12531 | 1.4389 | 1.0818 | 0.099209
UC Santa Cruz | 39.3203 | 7.2203 | 0.14684 | 1.4389 | 1.0278 | 0.099209
Housing Non-complex Space
UC Berkeley | 36.7464 | 5.1015 | 0.1934 | 0.97553 | 0.69681 | 0.14173
UC Davis | 39.6778 | 6.0572 | 0.19011 | 1.5139 | 1.1383 | 0.14173
UC Irvine | 35.2456 | 5.9058 | 0.15095 | 1.1655 | 0.87635 | 0.14173
UCLA | 34.9723 | 5.6116 | 0.15825 | 1.0389 | 0.7811 | 0.14173
UC Merced | 40.4974 | 6.5287 | 0.18221 | 1.5772 | 1.1859 | 0.14173
UC Riverside | 38.2068 | 6.3137 | 0.16664 | 1.5139 | 1.1383 | 0.14173
UC San Diego | 33.8415 | 5.5644 | 0.14856 | 1.0072 | 0.75729 | 0.14173
UCSF - Parnassus | 36.9957 | 5.0562 | 0.19744 | 0.91219 | 0.68586 | 0.14173
UCSF - Mission Bay | 37.4893 | 5.2008 | 0.19744 | 0.97553 | 0.69681 | 0.14173
UC Santa Barbara | 35.7419 | 5.2288 | 0.17901 | 1.0072 | 0.75729 | 0.14173
UC Santa Cruz | 38.2229 | 5.0542 | 0.20978 | 1.0072 | 0.71943 | 0.14173
Lab/Complex Space5
UC Berkeley | 199.0572 | 23.4246 | 1.1913 | 3.4354 | 2.4539 | 0.34247
UC Davis | 202.679 | 24.5668 | 1.1886 | 4.0789 | 3.0668 | 0.34247
UC Irvine | 198.7856 | 24.3858 | 1.1558 | 3.6625 | 2.7538 | 0.34247
UCLA | 198.1971 | 24.0343 | 1.1619 | 3.5111 | 2.6399 | 0.34247
UC Merced | 203.9417 | 25.1304 | 1.182 | 4.1546 | 3.1237 | 0.34247
UC Riverside | 201.7621 | 24.8734 | 1.1689 | 4.0789 | 3.0668 | 0.34247
UC San Diego | 197.1932 | 23.9778 | 1.1538 | 3.4733 | 2.6115 | 0.34247
UCSF - Parnassus | 199.2104 | 23.3704 | 1.1947 | 3.3597 | 2.5261 | 0.34247
UCSF - Mission Bay | 199.8003 | 23.5433 | 1.1947 | 3.4354 | 2.4539 | 0.34247
UC Santa Barbara | 198.3726 | 23.5767 | 1.1793 | 3.4733 | 2.6115 | 0.34247
UC Santa Cruz | 200.2347 | 23.3681 | 1.205 | 3.4733 | 2.4809 | 0.34247
100% Lab Space6
UC Berkeley | 359.7103 | 39.5613 | 2.2473 | 5.4772 | 3.9123 | 0.47591
UC Davis | 362.5261 | 40.4805 | 2.2441 | 5.995 | 4.5076 | 0.47591
UC Irvine | 358.2181 | 40.3349 | 2.206 | 5.66 | 4.2556 | 0.47591
UCLA | 357.9636 | 40.052 | 2.2131 | 5.5381 | 4.164 | 0.47591
UC Merced | 363.3055 | 40.9341 | 2.2364 | 6.056 | 4.5534 | 0.47591
UC Riverside | 361.0844 | 40.7273 | 2.2212 | 5.995 | 4.5076 | 0.47591
UC San Diego | 356.8648 | 40.0065 | 2.2036 | 5.5077 | 4.1411 | 0.47591
UCSF - Parnassus | 359.9547 | 39.5177 | 2.2512 | 5.4163 | 4.0724 | 0.47591
UCSF - Mission Bay | 360.4295 | 39.6568 | 2.2512 | 5.4772 | 3.9123 | 0.47591
UC Santa Barbara | 358.7276 | 39.6837 | 2.2333 | 5.5077 | 4.1411 | 0.47591
UC Santa Cruz | 361.1492 | 39.5158 | 2.2632 | 5.5077 | 3.934 | 0.47591
Building-Specific Adjustments
1 These values may be slightly lower than previously published values (i.e. for UC Merced) because they reflect load on the building meter instead of at the campus meter. To reflect load on campus meter, increase value by 1.05 (to account for distribution and transformation losses).
2 These values may be slightly lower than previously published values (i.e. for UC Merced) because they reflect load on the building meter instead of at the campus meter. To reflect load on campus meter, increase value by 1.05 (to account for distribution and transformation losses). For campuses with district chilled water, if a specific building has a chiller instead, increase value by (1/0.7).
3 In the case where a chiller is in the building, add the maximum chilled water value to the maximum power value by multiplying the chilled water value times 0.6 kW/ton.
4 These benchmarks are directly applicable to buildings with boilers in the building or connected to (low-loss) district hot water systems (non-steam). These benchmarks can be applicable to building design for buildings connected to district steam systems with the understanding that additional losses characteristic of steam systems will impact actual building energy performance during operations. For example, 50% extra use from trap/exchanger losses within the building plus 50% extra use from trap/leakage losses in distribution systems has been commonly observed.
5 Values shown are valid for complex space consisting of 50% lab use and 50% academic / administrative use. For additional information on calculating EUI for different levels of complex space see "100% Lab Space" values.
6 The 100% Lab Space benchmark values are provided for use in creating a custom benchmark and target when a building project contains significantly more or less lab space than the 50% lab use and 50% academic/administrative use outlined in the Lab/Complex Space section.

## 2017-20
|  | Provided for Reference Only |  |  | Provided for Reference Only
See 2015-16 Benchmark for max. power, chilled water, and thermal reference values | 2017-18 Compliance Target - 60% of Benchmark Site Energy (kBtu/yr/GSF) | Annual Electricity1 | Annual Thermal4 | 2019-20 Compliance Target - 55% of Benchmark Site Energy (kBtu/yr/GSF) | Annual Electricity1 | Annual Thermal4
|  | kWh/yr/GSF | therms/yr/GSF |  | kWh/yr/GSF | therms/yr/GSF
|  | Including Prorated Part of Plant Use and Site Lighting | Including Prorated Part of Plant Use |  | Including Prorated Part of Plant Use and Site Lighting | Including Prorated Part of Plant Use
Academic/Administrative Non-complex Space
UC Berkeley | 35.45 | 6.7272 | 0.12497 | 32.4959 | 6.1666 | 0.11455
UC Davis | 39.5371 | 7.9875 | 0.12284 | 36.2423 | 7.3218 | 0.1126
UC Irvine | 36.3258 | 7.7878 | 0.097538 | 33.2987 | 7.1388 | 0.08941
UCLA | 35.4743 | 7.4 | 0.10226 | 32.5181 | 6.7833 | 0.093735
UC Merced | 41.1488 | 8.6093 | 0.11774 | 37.7198 | 7.8919 | 0.10793
UC Riverside | 39.1752 | 8.3257 | 0.10768 | 35.9106 | 7.6319 | 0.098705
UC San Diego | 34.6352 | 7.3376 | 0.095992 | 31.7489 | 6.7262 | 0.087992
UCSF - Parnassus | 35.5071 | 6.6675 | 0.12758 | 32.5482 | 6.1118 | 0.11695
UCSF - Mission Bay | 36.158 | 6.8582 | 0.12758 | 33.1448 | 6.2867 | 0.11695
UC Santa Barbara | 35.0931 | 6.8951 | 0.11567 | 32.1686 | 6.3205 | 0.10603
UC Santa Cruz | 36.2956 | 6.6649 | 0.13555 | 33.271 | 6.1095 | 0.12425
Housing Non-complex Space
UC Berkeley | 33.9197 | 4.7091 | 0.17852 | 31.0931 | 4.3166 | 0.16365
UC Davis | 36.6256 | 5.5912 | 0.17548 | 33.5735 | 5.1253 | 0.16086
UC Irvine | 32.5344 | 5.4515 | 0.13934 | 29.8232 | 4.9972 | 0.12773
UCLA | 32.2821 | 5.18 | 0.14608 | 29.592 | 4.7483 | 0.13391
UC Merced | 37.3822 | 6.0265 | 0.1682 | 34.2671 | 5.5243 | 0.15418
UC Riverside | 35.2678 | 5.828 | 0.15383 | 32.3288 | 5.3423 | 0.14101
UC San Diego | 31.2383 | 5.1364 | 0.13713 | 28.6351 | 4.7083 | 0.1257
UCSF - Parnassus | 34.1499 | 4.6672 | 0.18225 | 31.3041 | 4.2783 | 0.16707
UCSF - Mission Bay | 34.6055 | 4.8008 | 0.18225 | 31.7217 | 4.4007 | 0.16707
UC Santa Barbara | 32.9925 | 4.8266 | 0.16524 | 30.2432 | 4.4244 | 0.15147
UC Santa Cruz | 35.2826 | 4.6654 | 0.19364 | 32.3424 | 4.2767 | 0.1775
Lab/Complex Space5
UC Berkeley | 183.7451 | 21.6227 | 1.0997 | 168.433 | 19.8208 | 1.008
UC Davis | 187.0883 | 22.6771 | 1.0971 | 171.4976 | 20.7873 | 1.0057
UC Irvine | 183.4944 | 22.51 | 1.0669 | 168.2032 | 20.6342 | 0.97799
UCLA | 182.9511 | 22.1855 | 1.0725 | 167.7052 | 20.3367 | 0.98316
UC Merced | 188.2539 | 23.1973 | 1.091 | 172.5661 | 21.2642 | 1.0001
UC Riverside | 186.2419 | 22.9601 | 1.079 | 170.7218 | 21.0467 | 0.9891
UC San Diego | 182.0245 | 22.1334 | 1.0651 | 166.8558 | 20.2889 | 0.9763
UCSF - Parnassus | 183.8865 | 21.5727 | 1.1028 | 168.5626 | 19.7749 | 1.0109
UCSF - Mission Bay | 184.4311 | 21.7323 | 1.1028 | 169.0618 | 19.9212 | 1.0109
UC Santa Barbara | 183.1131 | 21.7631 | 1.0886 | 167.8537 | 19.9495 | 0.99786
UC Santa Cruz | 184.8321 | 21.5705 | 1.1123 | 169.4294 | 19.773 | 1.0196
100% Lab Space6
UC Berkeley | 332.0403 | 36.5181 | 2.0744 | 304.3702 | 33.4749 | 1.9015
UC Davis | 334.6395 | 37.3666 | 2.0714 | 306.7529 | 34.2527 | 1.8988
UC Irvine | 330.6629 | 37.2322 | 2.0363 | 303.1077 | 34.1295 | 1.8666
UCLA | 330.428 | 36.9711 | 2.0428 | 302.8923 | 33.8901 | 1.8726
UC Merced | 335.359 | 37.7853 | 2.0644 | 307.4124 | 34.6366 | 1.8923
UC Riverside | 333.3087 | 37.5944 | 2.0504 | 305.5329 | 34.4615 | 1.8795
UC San Diego | 329.4137 | 36.9291 | 2.0341 | 301.9626 | 33.8517 | 1.8646
UCSF - Parnassus | 332.2659 | 36.4779 | 2.078 | 304.5771 | 33.438 | 1.9049
UCSF - Mission Bay | 332.7041 | 36.6063 | 2.078 | 304.9788 | 33.5558 | 1.9049
UC Santa Barbara | 331.1332 | 36.6311 | 2.0615 | 303.5388 | 33.5785 | 1.8897
UC Santa Cruz | 333.3685 | 36.4761 | 2.0891 | 305.5878 | 33.4365 | 1.915
Building-Specific Adjustments
1 These values may be slightly lower than previously published values (i.e. for UC Merced) because they reflect load on the building meter instead of at the campus meter. To reflect load on campus meter, increase value by 1.05 (to account for distribution and transformation losses).
4 These benchmarks are directly applicable to buildings with boilers in the building or connected to (low-loss) district hot water systems (non-steam). These benchmarks can be applicable to building design for buildings connected to district steam systems with the understanding that additional losses characteristic of steam systems will impact actual building energy performance during operations. For example, 50% extra use from trap/exchanger losses within the building plus 50% extra use from trap/leakage losses in distribution systems has been commonly observed.
5 Values shown are valid for complex space consisting of 50% lab use and 50% academic / administrative use. For additional information on calculating EUI for different levels of complex space see "100% Lab Space" values.
6 The 100% Lab Space benchmark values are provided for use in creating a custom benchmark and target when a building project contains significantly more or less lab space than the 50% lab use and 50% academic/administrative use outlined in the Lab/Complex Space section.

## 2021-24
|  | Provided for Reference Only |  |  | Provided for Reference Only
See 2015-16 Benchmark for max. power, chilled water, and thermal reference values | 2021-22 Compliance Target, 2015-16 Stretch Target - 50% of Benchmark Site Energy (kBtu/yr/GSF) | Annual Electricity1 | Annual Thermal4 | 2023-24 Compliance Target, 2017-18 Stretch Target - 45% of Benchmark Site Energy (kBtu/yr/GSF) | Annual Electricity1 | Annual Thermal4
|  | kWh/yr/GSF | therms/yr/GSF |  | kWh/yr/GSF | therms/yr/GSF
|  | Including Prorated Part of Plant Use and Site Lighting | Including Prorated Part of Plant Use |  | Including Prorated Part of Plant Use and Site Lighting | Including Prorated Part of Plant Use
Academic/Administrative Non-complex Space
UC Berkeley | 29.5417 | 5.606 | 0.10414 | 26.5875 | 5.0454 | 0.093725
UC Davis | 32.9476 | 6.6562 | 0.10237 | 29.6528 | 5.9906 | 0.092129
UC Irvine | 30.2715 | 6.4898 | 0.081282 | 27.2444 | 5.8409 | 0.073153
UCLA | 29.5619 | 6.1666 | 0.085214 | 26.6057 | 5.55 | 0.076692
UC Merced | 34.2907 | 7.1744 | 0.098115 | 30.8616 | 6.457 | 0.088304
UC Riverside | 32.646 | 6.9381 | 0.089732 | 29.3814 | 6.2443 | 0.080759
UC San Diego | 28.8627 | 6.1147 | 0.079993 | 25.9764 | 5.5032 | 0.071994
UCSF - Parnassus | 29.5893 | 5.5562 | 0.10631 | 26.6303 | 5.0006 | 0.095683
UCSF - Mission Bay | 30.1316 | 5.7152 | 0.10631 | 27.1185 | 5.1437 | 0.095683
UC Santa Barbara | 29.2442 | 5.7459 | 0.096392 | 26.3198 | 5.1713 | 0.086752
UC Santa Cruz | 30.2464 | 5.5541 | 0.11296 | 27.2217 | 4.9987 | 0.10166
Housing Non-complex Space
UC Berkeley | 28.2665 | 3.9242 | 0.14877 | 25.4398 | 3.5318 | 0.13389
UC Davis | 30.5214 | 4.6594 | 0.14624 | 27.4692 | 4.1934 | 0.13161
UC Irvine | 27.112 | 4.5429 | 0.11612 | 24.4008 | 4.0886 | 0.1045
UCLA | 26.9018 | 4.3166 | 0.12173 | 24.2116 | 3.885 | 0.10956
UC Merced | 31.1519 | 5.0221 | 0.14016 | 28.0367 | 4.5199 | 0.12615
UC Riverside | 29.3898 | 4.8567 | 0.12819 | 26.4508 | 4.371 | 0.11537
UC San Diego | 26.0319 | 4.2803 | 0.11428 | 23.4287 | 3.8523 | 0.10285
UCSF - Parnassus | 28.4583 | 3.8894 | 0.15188 | 25.6124 | 3.5004 | 0.13669
UCSF - Mission Bay | 28.8379 | 4.0006 | 0.15188 | 25.9541 | 3.6006 | 0.13669
UC Santa Barbara | 27.4938 | 4.0221 | 0.1377 | 24.7444 | 3.6199 | 0.12393
UC Santa Cruz | 29.4022 | 3.8879 | 0.16137 | 26.462 | 3.4991 | 0.14523
Lab/Complex Space5
UC Berkeley | 153.121 | 18.0189 | 0.91641 | 137.8089 | 16.217 | 0.82476
UC Davis | 155.9069 | 18.8975 | 0.91429 | 140.3162 | 17.0078 | 0.82286
UC Irvine | 152.912 | 18.7583 | 0.88909 | 137.6208 | 16.8825 | 0.80018
UCLA | 152.4593 | 18.4879 | 0.89378 | 137.2134 | 16.6391 | 0.80441
UC Merced | 156.8782 | 19.3311 | 0.9092 | 141.1904 | 17.398 | 0.81828
UC Riverside | 155.2016 | 19.1334 | 0.89919 | 139.6815 | 17.2201 | 0.80927
UC San Diego | 151.687 | 18.4445 | 0.88755 | 136.5183 | 16.6 | 0.79879
UCSF - Parnassus | 153.2388 | 17.9772 | 0.919 | 137.9149 | 16.1795 | 0.8271
UCSF - Mission Bay | 153.6925 | 18.1102 | 0.919 | 138.3233 | 16.2992 | 0.8271
UC Santa Barbara | 152.5943 | 18.1359 | 0.90714 | 137.3348 | 16.3223 | 0.81643
UC Santa Cruz | 154.0267 | 17.9754 | 0.92695 | 138.624 | 16.1779 | 0.83425
100% Lab Space6
UC Berkeley | 311.2736 | 30.4317 | 2.0744 | 249.0302 | 27.3886 | 1.5558
UC Davis | 278.8663 | 31.1389 | 1.7262 | 250.9796 | 28.025 | 1.5536
UC Irvine | 275.5524 | 31.0268 | 1.6969 | 247.9972 | 27.9242 | 1.5272
UCLA | 275.3566 | 30.8092 | 1.7024 | 247.821 | 27.7283 | 1.5321
UC Merced | 279.4658 | 31.4878 | 1.7203 | 251.5192 | 28.339 | 1.5483
UC Riverside | 277.7572 | 31.3287 | 1.7086 | 249.9815 | 28.1958 | 1.5378
UC San Diego | 274.5114 | 30.7742 | 1.6951 | 247.0603 | 27.6968 | 1.5256
UCSF - Parnassus | 276.8883 | 30.3982 | 1.7317 | 249.1994 | 27.3584 | 1.5585
UCSF - Mission Bay | 277.2534 | 30.5052 | 1.7317 | 249.5281 | 27.4547 | 1.5585
UC Santa Barbara | 275.9443 | 30.5259 | 1.7179 | 248.3499 | 27.4733 | 1.5461
UC Santa Cruz | 277.8071 | 30.3968 | 1.7409 | 250.0264 | 27.3571 | 1.5668
Building-Specific Adjustments
1 These values may be slightly lower than previously published values (i.e. for UC Merced) because they reflect load on the building meter instead of at the campus meter. To reflect load on campus meter, increase value by 1.05 (to account for distribution and transformation losses).
4 These benchmarks are directly applicable to buildings with boilers in the building or connected to (low-loss) district hot water systems (non-steam). These benchmarks can be applicable to building design for buildings connected to district steam systems with the understanding that additional losses characteristic of steam systems will impact actual building energy performance during operations. For example, 50% extra use from trap/exchanger losses within the building plus 50% extra use from trap/leakage losses in distribution systems has been commonly observed.
5 Values shown are valid for complex space consisting of 50% lab use and 50% academic / administrative use. For additional information on calculating EUI for different levels of complex space see "100% Lab Space" values.
6 The 100% Lab Space benchmark values are provided for use in creating a custom benchmark and target when a building project contains significantly more or less lab space than the 50% lab use and 50% academic/administrative use outlined in the Lab/Complex Space section.

## 2022-25
|  | Provided for Reference Only |  |  | Provided for Reference Only
See 2015-16 Benchmark for max. power, chilled water, and thermal reference values | 2025+ Compliance Target, 2019-20 Stretch Target - 40% of Benchmark Site Energy (kBtu/yr/GSF) | Annual Electricity1 | Annual Thermal4 | 2021-22 Stretch Target - 35% of Benchmark Site Energy (kBtu/yr/GSF) | Annual Electricity1 | Annual Thermal4
|  | kWh/yr/GSF | therms/yr/GSF |  | kWh/yr/GSF | therms/yr/GSF
|  | Including Prorated Part of Plant Use and Site Lighting | Including Prorated Part of Plant Use |  | Including Prorated Part of Plant Use and Site Lighting | Including Prorated Part of Plant Use
Academic/Administrative Non-complex Space
UC Berkeley | 23.6334 | 4.4848 | 0.083311 | 20.6792 | 3.9242 | 0.072897
UC Davis | 26.3581 | 5.325 | 0.081892 | 23.0633 | 4.6594 | 0.071656
UC Irvine | 24.2172 | 5.1919 | 0.065025 | 21.1901 | 4.5429 | 0.056897
UCLA | 23.6495 | 4.9333 | 0.068171 | 20.6933 | 4.3166 | 0.05965
UC Merced | 27.4325 | 5.7395 | 0.078492 | 24.0035 | 5.0221 | 0.068681
UC Riverside | 26.1168 | 5.5505 | 0.071785 | 22.8522 | 4.8567 | 0.062812
UC San Diego | 23.0901 | 4.8918 | 0.063994 | 20.2039 | 4.2803 | 0.055995
UCSF - Parnassus | 23.6714 | 4.445 | 0.085052 | 20.7125 | 3.8894 | 0.07442
UCSF - Mission Bay | 24.1053 | 4.5721 | 0.085052 | 21.0922 | 4.0006 | 0.07442
UC Santa Barbara | 23.3954 | 4.5967 | 0.077113 | 20.471 | 4.0221 | 0.067474
UC Santa Cruz | 24.1971 | 4.4433 | 0.090366 | 21.1724 | 3.8879 | 0.07907
Housing Non-complex Space
UC Berkeley | 22.6132 | 3.1394 | 0.11902 | 19.7865 | 2.747 | 0.10414
UC Davis | 24.4171 | 3.7275 | 0.11699 | 21.3649 | 3.2616 | 0.10237
UC Irvine | 21.6896 | 3.6343 | 0.092893 | 18.9784 | 3.18 | 0.081282
UCLA | 21.5214 | 3.4533 | 0.097387 | 18.8312 | 3.0216 | 0.085214
UC Merced | 24.9215 | 4.0177 | 0.11213 | 21.8063 | 3.5155 | 0.098115
UC Riverside | 23.5119 | 3.8853 | 0.10255 | 20.5729 | 3.3997 | 0.089732
UC San Diego | 20.8255 | 3.4242 | 0.091421 | 18.2224 | 2.9962 | 0.079993
UCSF - Parnassus | 22.7666 | 3.1115 | 0.1215 | 19.9208 | 2.7225 | 0.10631
UCSF - Mission Bay | 23.0703 | 3.2005 | 0.1215 | 20.1865 | 2.8004 | 0.10631
UC Santa Barbara | 21.995 | 3.2177 | 0.11016 | 19.2456 | 2.8155 | 0.096392
UC Santa Cruz | 23.5218 | 3.1103 | 0.12909 | 20.5815 | 2.7215 | 0.11296
Lab/Complex Space5
UC Berkeley | 122.4968 | 14.4151 | 0.73312 | 107.1847 | 12.6132 | 0.64148
UC Davis | 124.7255 | 15.118 | 0.73143 | 109.1348 | 13.2283 | 0.64
UC Irvine | 122.3296 | 15.0067 | 0.71127 | 107.0384 | 13.1308 | 0.62236
UCLA | 121.9674 | 14.7903 | 0.71503 | 106.7215 | 12.9415 | 0.62565
UC Merced | 125.5026 | 15.4649 | 0.72736 | 109.8148 | 13.5318 | 0.63644
UC Riverside | 124.1613 | 15.3067 | 0.71935 | 108.6411 | 13.3934 | 0.62943
UC San Diego | 121.3496 | 14.7556 | 0.71004 | 106.1809 | 12.9111 | 0.62128
UCSF - Parnassus | 122.591 | 14.3818 | 0.7352 | 107.2671 | 12.5841 | 0.6433
UCSF - Mission Bay | 122.954 | 14.4882 | 0.7352 | 107.5848 | 12.6771 | 0.6433
UC Santa Barbara | 122.0754 | 14.5087 | 0.72572 | 106.816 | 12.6951 | 0.635
UC Santa Cruz | 123.2214 | 14.3804 | 0.74156 | 107.8187 | 12.5828 | 0.64886
100% Lab Space6
UC Berkeley | 221.3602 | 24.3454 | 1.3829 | 193.6901 | 21.3022 | 1.2101
UC Davis | 223.093 | 24.9111 | 1.381 | 195.2064 | 21.7972 | 1.2083
UC Irvine | 220.4419 | 24.8215 | 1.3575 | 192.8867 | 21.7188 | 1.1878
UCLA | 220.2853 | 24.6474 | 1.3619 | 192.7496 | 21.5664 | 1.1916
UC Merced | 223.5726 | 25.1902 | 1.3762 | 195.6261 | 22.0414 | 1.2042
UC Riverside | 222.2058 | 25.0629 | 1.3669 | 194.4301 | 21.9301 | 1.196
UC San Diego | 219.6091 | 24.6194 | 1.3561 | 192.158 | 21.542 | 1.1866
UCSF - Parnassus | 221.5106 | 24.3186 | 1.3854 | 193.8218 | 21.2787 | 1.2122
UCSF - Mission Bay | 221.8028 | 24.4042 | 1.3854 | 194.0774 | 21.3537 | 1.2122
UC Santa Barbara | 220.7555 | 24.4207 | 1.3743 | 193.161 | 21.3682 | 1.2025
UC Santa Cruz | 222.2457 | 24.3174 | 1.3927 | 194.465 | 21.2777 | 1.2187
Building-Specific Adjustments
1 These values may be slightly lower than previously published values (i.e. for UC Merced) because they reflect load on the building meter instead of at the campus meter. To reflect load on campus meter, increase value by 1.05 (to account for distribution and transformation losses).
4 These benchmarks are directly applicable to buildings with boilers in the building or connected to (low-loss) district hot water systems (non-steam). These benchmarks can be applicable to building design for buildings connected to district steam systems with the understanding that additional losses characteristic of steam systems will impact actual building energy performance during operations. For example, 50% extra use from trap/exchanger losses within the building plus 50% extra use from trap/leakage losses in distribution systems has been commonly observed.
5 Values shown are valid for complex space consisting of 50% lab use and 50% academic / administrative use. For additional information on calculating EUI for different levels of complex space see "100% Lab Space" values.
6 The 100% Lab Space benchmark values are provided for use in creating a custom benchmark and target when a building project contains significantly more or less lab space than the 50% lab use and 50% academic/administrative use outlined in the Lab/Complex Space section.

## 2023-25 Stretch Targets
|  | Provided for Reference Only |  |  | Provided for Reference Only
See 2015-16 Benchmark for max. power, chilled water, and thermal reference values | 2023-24 Stretch Target - 30% of Benchmark Site Energy (kBtu/yr/GSF) | Annual Electricity1 | Annual Thermal4 | 2025+ Stretch Target - 25% of Benchmark Site Energy (kBtu/yr/GSF) | Annual Electricity1 | Annual Thermal4
|  | kWh/yr/GSF | therms/yr/GSF |  | kWh/yr/GSF | therms/yr/GSF
|  | Including Prorated Part of Plant Use and Site Lighting | Including Prorated Part of Plant Use |  | Including Prorated Part of Plant Use and Site Lighting | Including Prorated Part of Plant Use
Academic/Administrative Non-complex Space
UC Berkeley | 17.725 | 3.3636 | 0.062483 | 14.7708 | 2.803 | 0.05207
UC Davis | 19.7685 | 3.9937 | 0.061419 | 16.4738 | 3.3281 | 0.051183
UC Irvine | 18.1629 | 3.8939 | 0.048769 | 15.1358 | 3.2449 | 0.040641
UCLA | 17.7372 | 3.7 | 0.051128 | 14.781 | 3.0833 | 0.042607
UC Merced | 20.5744 | 4.3047 | 0.058869 | 17.1453 | 3.5872 | 0.049058
UC Riverside | 19.5876 | 4.1629 | 0.053839 | 16.323 | 3.4691 | 0.044866
UC San Diego | 17.3176 | 3.6688 | 0.047996 | 14.4313 | 3.0574 | 0.039997
UCSF - Parnassus | 17.7536 | 3.3337 | 0.063789 | 14.7946 | 2.7781 | 0.053157
UCSF - Mission Bay | 18.079 | 3.4291 | 0.063789 | 15.0658 | 2.8576 | 0.053157
UC Santa Barbara | 17.5465 | 3.4475 | 0.057835 | 14.6221 | 2.873 | 0.048196
UC Santa Cruz | 18.1478 | 3.3325 | 0.067774 | 15.1232 | 2.7771 | 0.056479
Housing Non-complex Space
UC Berkeley | 16.9599 | 2.3545 | 0.089262 | 14.1332 | 1.9621 | 0.074385
UC Davis | 18.3128 | 2.7956 | 0.087742 | 15.2607 | 2.3297 | 0.073118
UC Irvine | 16.2672 | 2.7257 | 0.06967 | 13.556 | 2.2714 | 0.058058
UCLA | 16.1411 | 2.59 | 0.07304 | 13.4509 | 2.1583 | 0.060867
UC Merced | 18.6911 | 3.0133 | 0.084099 | 15.5759 | 2.5111 | 0.070082
UC Riverside | 17.6339 | 2.914 | 0.076913 | 14.6949 | 2.4283 | 0.064094
UC San Diego | 15.6192 | 2.5682 | 0.068565 | 13.016 | 2.1401 | 0.057138
UCSF - Parnassus | 17.075 | 2.3336 | 0.091127 | 14.2291 | 1.9447 | 0.075939
UCSF - Mission Bay | 17.3027 | 2.4004 | 0.091127 | 14.419 | 2.0003 | 0.075939
UC Santa Barbara | 16.4963 | 2.4133 | 0.082621 | 13.7469 | 2.0111 | 0.068851
UC Santa Cruz | 17.6413 | 2.3327 | 0.096821 | 14.7011 | 1.9439 | 0.080684
Lab/Complex Space5
UC Berkeley | 91.8726 | 10.8113 | 0.54984 | 76.5605 | 9.0094 | 0.4582
UC Davis | 93.5442 | 11.3385 | 0.54857 | 77.9535 | 9.4488 | 0.45714
UC Irvine | 91.7472 | 11.255 | 0.53345 | 76.456 | 9.3792 | 0.44454
UCLA | 91.4756 | 11.0928 | 0.53627 | 76.2296 | 9.244 | 0.44689
UC Merced | 94.1269 | 11.5987 | 0.54552 | 78.4391 | 9.6656 | 0.4546
UC Riverside | 93.121 | 11.48 | 0.53951 | 77.6008 | 9.5667 | 0.44959
UC San Diego | 91.0122 | 11.0667 | 0.53253 | 75.8435 | 9.2222 | 0.44377
UCSF - Parnassus | 91.9433 | 10.7863 | 0.5514 | 76.6194 | 8.9886 | 0.4595
UCSF - Mission Bay | 92.2155 | 10.8661 | 0.5514 | 76.8463 | 9.0551 | 0.4595
UC Santa Barbara | 91.5566 | 10.8816 | 0.54429 | 76.2971 | 9.068 | 0.45357
UC Santa Cruz | 92.416 | 10.7853 | 0.55617 | 77.0134 | 8.9877 | 0.46347
100% Lab Space6
UC Berkeley | 166.0201 | 18.259 | 1.0372 | 138.3501 | 15.2159 | 0.86434
UC Davis | 167.3198 | 18.6833 | 1.0357 | 139.4331 | 15.5694 | 0.8631
UC Irvine | 165.3315 | 18.6161 | 1.0181 | 137.7762 | 15.5134 | 0.84844
UCLA | 165.214 | 18.4855 | 1.0214 | 137.6783 | 15.4046 | 0.85118
UC Merced | 167.6795 | 18.8927 | 1.0322 | 139.7329 | 15.7439 | 0.86015
UC Riverside | 166.6543 | 18.7972 | 1.0252 | 138.8786 | 15.6643 | 0.85432
UC San Diego | 164.7069 | 18.4645 | 1.0171 | 137.2557 | 15.3871 | 0.84755
UCSF - Parnassus | 166.133 | 18.2389 | 1.039 | 138.4441 | 15.1991 | 0.86585
UCSF - Mission Bay | 166.3521 | 18.3031 | 1.039 | 138.6267 | 15.2526 | 0.86585
UC Santa Barbara | 165.5666 | 18.3156 | 1.0307 | 137.9722 | 15.263 | 0.85895
UC Santa Cruz | 166.6842 | 18.2381 | 1.0446 | 138.9035 | 15.1984 | 0.87047
Building-Specific Adjustments
1 These values may be slightly lower than previously published values (i.e. for UC Merced) because they reflect load on the building meter instead of at the campus meter. To reflect load on campus meter, increase value by 1.05 (to account for distribution and transformation losses).
4 These benchmarks are directly applicable to buildings with boilers in the building or connected to (low-loss) district hot water systems (non-steam). These benchmarks can be applicable to building design for buildings connected to district steam systems with the understanding that additional losses characteristic of steam systems will impact actual building energy performance during operations. For example, 50% extra use from trap/exchanger losses within the building plus 50% extra use from trap/leakage losses in distribution systems has been commonly observed.
5 Values shown are valid for complex space consisting of 50% lab use and 50% academic / administrative use. For additional information on calculating EUI for different levels of complex space see "100% Lab Space" values.
6 The 100% Lab Space benchmark values are provided for use in creating a custom benchmark and target when a building project contains significantly more or less lab space than the 50% lab use and 50% academic/administrative use outlined in the Lab/Complex Space section.

## Source Data
| Max. Power | Max. Chilled Water | Annual Electricty | Max. Thermal | Annual Thermal
Berkeley | 3.0629 | 1.612 | 11.2121 | 0.12401 | 0.20828
Davis | 3.3272 | 2.5017 | 13.3125 | 0.12401 | 0.20473
Irvine | 2.5616 | 1.926 | 12.9797 | 0.12401 | 0.16256
Los Angeles | 2.2832 | 1.7167 | 12.3333 | 0.12401 | 0.17043
Merced | 3.4665 | 2.6064 | 14.3489 | 0.12401 | 0.19623
Riverside | 3.3272 | 2.5017 | 13.8762 | 0.12401 | 0.17946
San Diego | 2.2136 | 1.6644 | 12.2294 | 0.12401 | 0.15999
San Francisco Parnassus | 2.0048 | 1.5074 | 11.1124 | 0.12401 | 0.21263
San Francisco Mission Bay | 3.0629 | 1.612 | 11.4304 | 0.12401 | 0.21263
Santa Barbara | 2.2136 | 1.6644 | 11.4918 | 0.12401 | 0.19278
Santa Cruz | 3.1623 | 1.6644 | 11.1082 | 0.12401 | 0.22591
Housing Non-complex Space
Berkeley | 2.144 | 1.1284 | 7.8484 | 0.17716 | 0.29754
Davis | 2.3291 | 1.7512 | 9.3187 | 0.17716 | 0.29247
Irvine | 1.7931 | 1.3482 | 9.0858 | 0.17716 | 0.23223
Los Angeles | 1.5983 | 1.2017 | 8.6333 | 0.17716 | 0.24347
Merced | 2.4265 | 1.8244 | 10.0442 | 0.17716 | 0.28033
Riverside | 2.3291 | 1.7512 | 9.7134 | 0.17716 | 0.25638
San Diego | 1.5495 | 1.1651 | 8.5606 | 0.17716 | 0.22855
San Francisco Parnassus | 1.4034 | 1.0552 | 7.7787 | 0.17716 | 0.30376
San Francisco Mission Bay | 2.144 | 1.1284 | 8.0013 | 0.17716 | 0.30376
Santa Barbara | 1.5495 | 1.1651 | 8.0443 | 0.17716 | 0.2754
Santa Cruz | 2.2136 | 1.1651 | 7.7757 | 0.17716 | 0.32274
Lab/Complex Space
Berkeley | 7.5503 | 3.9739 | 36.0378 | 0.42809 | 1.8328
Davis | 6.2752 | 4.7182 | 37.7951 | 0.42809 | 1.8286
Irvine | 5.6346 | 4.2366 | 37.5167 | 0.42809 | 1.7782
Los Angeles | 5.4017 | 4.0614 | 36.9758 | 0.42809 | 1.7876
Merced | 6.3917 | 4.8058 | 38.6622 | 0.42809 | 1.8184
Riverside | 6.2752 | 4.7182 | 38.2668 | 0.42809 | 1.7984
San Diego | 5.3435 | 4.0177 | 36.8889 | 0.42809 | 1.7751
San Francisco Parnassus | 5.1688 | 3.8863 | 35.9544 | 0.42809 | 1.838
San Francisco Mission Bay | 7.5503 | 3.9739 | 36.2204 | 0.42809 | 1.838
Santa Barbara | 5.3435 | 4.0177 | 36.2719 | 0.42809 | 1.8143
Santa Cruz | 7.6335 | 4.0177 | 35.9509 | 0.42809 | 1.8539